## Sheet1
| P_S_HX-3402 | u_S_HX-3402 | P_S_HX-3402 | u_S_HX-3402 | P_S_HX-3330 | U_S_HX-3330 | P_S_HX-3504 | U_S_HX-3504 | P_S_HX-3504 | U_S_HX-3504 | P_S_HX-3702 | U_S_HX-3702
Name:
Tag:
Design data
First section | Process side | Utility side | Process side | Utility side | Process side | Utility side | Process side | Utility side | Process side | Utility side | Process side | Utility side
Fluid: | Clean air | Hot water | Clean air | Chilled water | Clean air | Dry saturated steam (p= 6 bar g) | Clean air | Dry saturated steam (p= 2 bar g) | Clean air | Dry saturated steam (p= 2 bar g) | Clean air | Hot water
Flow: | 57000 kg/h | 16400 kg/h | 5000 kg/h | should be calculated | 9000 kg/h | should be calculated | 5700 kg/h | Should be calculated | 5700 kg/h | Should be calculated | 80000 kg/h | 16400 kg/h
Inlet / outlet conditions: | In:5ºC,80 % RH Out: 37°C | In: 53ºC / Out: 26°C | In:30ºC, 70% RH Out: 5ºC, 100% RH | In: 1,5ºC / Out: 15ºC | In:10ºC Out: 130ºC | In:saturated steam (p= 6 bar g) Out: steam condensate (p( bar g)= 6 -∆p ) | In:10ºC Out: 80ºC | In:saturated steam (p= 2 bar g) Out: steam condensate (p( bar g)= 2 -∆p ) | In:10ºC Out: 80ºC | In:saturated steam (p= 2 bar g) Out: steam condensate (p( bar g)= 2 -∆p ) | In:70ºC Out: 47ºC | In: 26ºC Out: 53°C
Material | AISI 316 tubes with AISI 316 spiral fins (aerofin type) |  | AISI 316 tubes with AISI 316 spiral fins (Aerofin type) |  | AISI 316 tubes with AISI 316 spiral fins (Aerofin type) |  | AISI 316 tubes with AISI 316 spiral fins (Aerofin type) |  | AISI 316 tubes with AISI 316 spiral fins (Aerofin type) |  | AISI 316 tubes with AISI 430 spiral fins (aerofin type)
Connections | Flanged casing | by supplier | Flanged casing | by supplier | Flanged casing | by supplier | Flanged casing | by supplier | Flanged casing | by supplier | Flanged casing | Flanged
Total allowable pressure drop (both sections): | 120 mm w.c. | ∆p | 60 mm w.c. | ∆p | 80 mm w.c. | ∆p | 60 mm w.c. | ∆p | 60 mm w.c. | ∆p | 40 mm w.c. | ∆p
Second section | Process side | Utility side | Process side | Utility side
Fluid: | Clean air | Condensate from third section | Clean air | Dry saturated steam (p= 1 bar g)
Flow: | 57000 kg/h | calculated from third section | 5000 kg/h | should be calculated
Inlet / outlet conditions: | In:37ºC Out: 55ºC | In: Output from third section Out: should be calculated | In: 5ºC, 100% RH Out: 20ºC | In:saturated steam (p= 20 bar g) Out: steam condensate (p( bar g)= 20 -∆p )
Material: | AISI 316 tubes with AISI 316 spiral fins (Aerofin type) |  | AISI 316 tubes with AISI 316 spiral fins (Aerofin type)
Connections | Flanged casing | Flanged | Flanged casing | Flanged
Total allowable pressure drop (both sections): | 120 mm w.c. | ∆p | 60 mm w.c. | ∆p
Third section | Process side | Utility side
Fluid: | Clean air | Dry saturated steam (p= 20 barg)
Flow: | 57000 kg/h | should be calculated
Inlet / outlet conditions: | In: 55ºC Out: 208ºC | In:saturated steam (p= 20 bar g) Out: steam condensate (p( bar g)= 20 -∆p )
Material: | AISI 316 tubes with AISI 316 spiral fins (Aerofin type)
Connections | Flanged casing | Flanged
Total allowable pressure drop (through all sections): | 120 mm w.c. | ∆p